## Slide 1
ACMV Fundamentals
Author: Yang Hai Xiang
Editor: Wong Chee Keat
Basic Facilities Knowledge Package
Yr.2019

## Slide 2
ACMV Fundamental Knowledge
What is ACMV or HVAC?
  ACMV is an abbreviation of: Air Conditioning and Mechanical Ventilation
  HVAC is an abbreviation of: Heat, Ventilation and Air Conditioning
ACMV / HVAC systems provide forced ventilation of facilities with ‘conditioned’ air
Air conditioning implies control of Temperature (°C) and Humidity (%RH)
‘Conditioning’ may involve
  Heating & Cooling
  Humidification & Dehumidification
  Filtration

## Slide 3
ACMV Fundamental Knowledge
Why is ventilation necessary ?
  Air to breathe
      Prevents oxygen depletion
      Removal of gases
      Removal of Odours
  Comfortable Working Environment
      Usually removal of heat from:
        People
        Lights
        Equipment
  Contamination Control
      Airborne dust kept to a minimum
      Controlled particulate limits

## Slide 4
ACMV Fundamental Knowledge
Air change rates
  Supply and extract from a room leads to a “turnover” of air, known as the Room Air Change Rate
  Room Air Change Rate = Supply Air Volume Flow (air changes per hour)
Room Volume
  Higher air change rates give faster dilution and removal of airborne contaminants, and hence cleaner room conditions
  The sources of contamination are mainly but not limited to
    Outside Air
    Pollution
    Dust
    Pollen
  Equipment
    Non-viable particulates
    Lubricants
  Humans
    Viable particulates (EM)
    Non-viable particulates
    Breathing
    Perspiration

## Slide 5
ACMV Fundamental Knowledge
Cleanroom Industry Design Thumb Rule for ACR
ISO | Class | Fed 208 Control | Air Changes Rate per Hour
1 | - | Stringent | > 750
2 | - | Stringent | > 750
3 | 1 | Stringent | > 750
4 | 10 | Stringent | 500 - 600
5 | 100 | Stringent | 150 - 400
6 | 1,000 | Intermediate | 60 - 100
7 | 10,000 | Intermediate | 25 – 40
8 | 100,000 | Less Stringent | 10 - 15

## Slide 6
ACMV Fundamental Knowledge
The Psychrometric Chart
Psychrometry is the science dealing with the physical laws of air – water mixtures.
Properties of Air
  Dry-bulb temperature
  Wet-bulb temperature
  Dew-point temperature
  Relative humidity
  Humidity ratio
  Specific Volume
  Enthalpy

## Slide 7
ACMV Fundamental Knowledge – Air Properties
Dry Bulb Temperature (Tdb)
Dry-bulb temperatures are read from an ordinary thermometer that has a dry bulb
Wet Bulb Temperature (Twb)
Wet-bulb temperatures are read from a thermometer whose bulb is covered by a wet wick
Dew Point temperature (Tdp)
Dew-point temperature is the temperature at which moisture leaves the air and condenses on objects.

## Slide 8
ACMV Fundamental Knowledge – Air Properties
Saturated Air
When the dry-bulb, wet-bulb, and dew-point temperatures are the same, the air is saturated. It can hold no more moisture. When air is at a saturated condition, moisture entering the air displaces moisture within the air. The displaced moisture leaves the air in the form of fine droplets. When this condition occurs in nature, it is called fog.
Relative humidity (Φ),
is a comparison of the amount of moisture that a given amount of air is holding, to the amount of moisture that the same amount of air can hold, at the same dry-bulb temperature. Relative humidity is expressed as a percentage

## Slide 9
ACMV Fundamental Knowledge – Air Properties
Humidity ratio (ω)
Describes the actual weight of water in an air–water vapor mixture. In other words, it’s mass of water vapor present in a unit mass of dry air.
Sometimes called Absolute Humidity, Specific Humidity. Normally expressed as grams of moisture per kilogram of dry air.
Specific Volume (v)
Volume of air vapor mixture that contains unit mass of dry air. Normally expressed as cube meter moisture per kilogram of dry air.
Enthalpy (h)
Sum of the internal (heat) energy of the air vapor mixture. Also called heat content per unit mass. Normally expressed as kilojoules per kilogram of dry air.
If two properties of air are known, the remaining properties can be determined using psychrometric chart.

## Slide 10
ACMV Fundamental Knowledge – Exercise # 1
Please try the following question,
Considering a room which contains air at 1atm, 23 °C and 65% relative humidity. Using psychrometric chart to determine,
  Wet bulb temperature
  Absolute humidity
  Dew point temperature
  Specific volume
  Enthalpy

## Slide 11
Using the Psychrometric Chart
Determine the entering air condition
If outdoor air (B) is mixed with recirculated air (A), how to determine the mixed air condition?
First step, need to determine the ratio of mixtures.
e.g. Fresh air 1000CMH, and recirculated air 3000CMH.
FA = 1000 / (1000+3000) = 25%, RA = 75%
Second step, determine the dry bulb temperature.
30 °C x 0.25 = 7.5 °C sum up = 24.75 °C
23 °C x 0.75 = 17.25 °C
This point will falls on the line of AB, so from the psychrometric
chart you can get all other properties.

## Slide 12
ACMV Fundamentals – HVAC overview

## Slide 13
ACMV Fundamentals – HVAC overview

## Slide 14
Cleanroom ACMV design

## Slide 15
Sensible heat and Latent heat
The process of comfort heating and air conditioning is simply a transfer of energy from one substance to another. This energy can be classified as either sensible or latent heat energy.
Sensible heat is heat energy that, when added to or removed from a substance, results in a measurable change in dry-bulb temperature.
Changes in the latent heat content of a substance are associated with the addition or removal of moisture.

## Slide 16
Air-conditioning Space design
Step 1
  Calculate the heat load in the space
Step 2
  Determine the space air-condition requirement
Step 3
  Identify the supply air conditions
Step 4
  Determine the supply air flow

## Slide 17
Step 1 – Calculate the heat load in the space
Estimating of heat load involves a lot of factors,
    Building orientation
    Use of the space in the building
    Physical dimensions of the space
    Dimensions of columns and beams within the space
    Construction materials
    Surrounding conditions – presence of reflective surfaces, other buildings’ shading
    Window sizes and position
    Doors
    Presence of stairways, lifts and escalators
    Number and activity level of occupants
    Lighting and types
    Equipment, machines and appliances
    Ventilation
    Operation cycle of building

## Slide 18
Step 2 – Determine the space air-condition requirement
Comfort zone as mentioned earlier
User requirement
Energy efficient consideration
Example:
Dry bulb temperature – 23 °C
Relative Humidity - 60%
Coil curve
Sensible Heat Ratio
Apparatus Dew point Temperature
Simplified method (but no accurate):
On the psychrometric chart draw a cooling line from the space required point, the cross point with saturated line is the supply air condition.
For the given example, the supply air dry bulb temperature is around 14.6 °C, considering the accuracy and errors, to take the temperature as 14 °C.
Step 3 – Identify the supply air conditions

## Slide 19
Step 3 – Identify the supply air conditions

## Slide 20
Step 4 – Determine the supply air flow
If the heat load estimated is around 10kw for the given space,
Air flow rate = (0.83 x 10kw) / (23 – 14) =0.92 (m3/s) = 0.92x3600 = 3320 (m3/h)